April 4, 2008

Testing different foam prototypes. First test is of just YSH-70 side, just silicon heater powered of all prototype ie. center section of below

Water flow rate is 1 l/min for all measurements

Test conditions summarized in table below for Allcomp 1.

| Allcomp 1 | V | I | P | P/A | V | I | P | P/A | V | I | P | P/A | V | I | P | P/A |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Kapton heaters |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Silicon heater | 0 | 0 | 0.00 | 0.00 | 6.94 | 1.2 | 8.33 | 0.64 |  |  |  |  |  |  |  |  |
| Tin | 20.1 | 20.1 |  |  |
| Tout | 20 | 20.2 |  |  |
| File # | 120 | 121 |  |  |

File 120

Label	Emis	BG	Ave	SD	Max	Min	Unit

A2	0.95	19.0	20.85	0.12	21.0	20.6	C

A3	0.95	19.0	20.78	0.25	21.6	20.5	C

Note that IR is a bit higher than direct fluid measurement by <1C.

File 121

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	30.65	1.17	32.2	27.8	C

A2	0.95	19.0	30.71	0.86	32.1	28.1	C

Cold	0.95	19.0	20.75	0.00	20.8	20.8	C

This implies delta T from fluid(direct measurement) of 30.7-20=10.7=11C or from IR it would be 30.7-20.8=9.9=10C. Thus 10-11C, in agreement about with previous measurements some months ago.

Next is Allcomp 2 prototype

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	20.41	0.12	20.8	20.1	C

A2	0.95	19.0	20.44	0.17	21.0	20.3	C

Looks like heater non-uniformity below....

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	29.02	0.62	30.1	26.9	C

A3	0.95	19.0	30.91	1.58	33.8	27.1	C

POCO

| POCO | V | I | P | P/A | V | I | P | P/A | V | I | P | P/A |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Kapton heaters |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Silicon heater | 0 | 0 | 0.00 | 0.00 | 6.93 | 1.2 | 8.35 | 0.64 |  |  |  |  |  |  |  |  |
| Tin | 20.2 | 20.2 |  |  |
| Tout | 20 | 20.1 |  |  |
| File # | 124 | 125 |  |  |

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	20.84	0.12	21.3	20.6	C

A2	0.95	19.0	20.83	0.12	21.3	20.5	C

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	31.48	0.90	32.9	27.3	C

A2	0.95	19.0	32.66	1.12	34.5	29.0	C

Koppers

| Koppers | V | I | P | P/A | V | I | P | P/A | V | I | P | P/A |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Kapton heaters |  |  |  |  |  |  |  |  |  |  |  |  |
| Silicon heater | 0 | 0 | 0.00 | 0.00 | 6.92 | 1.2 | 8.37 | 0.64 |  |  |  |  |
| Tin | 20.1 | 20.2 |  |
| Tout | 20 | 20.2 |  |
| File # | 126 | 127 |  |

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	20.63	0.13	21.3	20.4	C

A2	0.95	19.0	20.60	0.11	20.9	20.4	C

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	28.92	0.82	29.9	26.1	C

A2	0.95	19.0	29.20	1.05	30.4	26.3	C

Two different values for Allcomp 2 in table below. One(29 twice) I ignore apparent hot spot on heater. Other entry I don’t.

April 18, 2008

Copper kapton heaters were attached to the other side of the three small samples and imaged. Also re-imaged the sides with silicon heaters.

Allcomp 2

File 132

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	19.66	0.16	20.3	19.3	C

File 133

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	29.53	7.17	42.8	21.3	C

File 135

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	19.75	0.31	21.0	19.3	C

File 134

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	28.28	1.83	31.8	22.6	C

POCO

File 128

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	20.04	0.45	21.8	19.6	C

File 129

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	31.64	8.49	48.0	21.8	C

File 130

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	19.83	0.21	21.1	19.6	C

File 131

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	29.51	2.52	33.3	22.9	C

Koppers

File 136

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	19.38	0.15	19.8	19.0	C

File 137

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	30.82	7.90	45.7	21.1	C

File 138

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	19.46	0.15	20.1	19.3	C

File 139

Label	Emis	BG	Ave	SD	Max	Min	Unit

A1	0.95	19.0	26.97	2.03	29.4	21.5	C

Looking at silicon again. DT to 0 pwr was 8.6,11.2 and 8.4 for Allcomp2, POCO, Koppers, respectively but using difference boxes to estimate temperature. Note also this time that agreement between water temperature and 0 power is much better. I don’t know why. Ambient or calibration?

Average copper-kapton temperatures are 29.5, 31.6 and 30.8 for Allcomp2, POCO and Koppers, respectively. Don’t learn much from this.